# FINDINGS OF FACT

After review of the air emission license amendment and renewal application, staff investigation reports, and other documents in the applicant’s file in the Bureau of Air Quality, pursuant to 38 Maine Revised Statutes (M.R.S.) § 344 and § 590, the Maine Department of Environmental Protection (Department) finds the following facts:

## REGISTRATION

### Introduction

MaineGeneral Medical Center (MaineGeneral) has applied to renew their Air Emission License for the operation of emission sources associated with their healthcare facilities.

The equipment addressed in this license is located at 35 Medical Center Parkway, Augusta, Maine.

MaineGeneral has requested an after-the-fact amendment to their license in order to replace Generator #1 with a new unit, Generator #5.

### Emission Equipment

The following equipment is addressed in this air emission license:

Boilers

| ### Equipment | Max. Capacity (MMBtu/hr) | Maximum Firing Rate | Fuel Type | Date of Manuf. | ### Date of Install. | ### Stack # |
| --- | --- | --- | --- | --- | --- | --- |
| Boiler #3 | 24.5 | 24,500 scf/hr 271 gal/hr | Natural Gas Propane | 2012 | ### 2012 | ### 2 |
| Boiler #4 | 24.5 | 24,500 scf/hr 271 gal/hr | Natural Gas Propane | 2012 | ### 2012 | ### 2 |
| Boiler #5 | 24.5 | 24,500 scf/hr 271 gal/hr | Natural Gas Propane | 2012 | ### 2012 | ### 2 |
| Boiler #6 | 1.0 | 980 scf/hr | Natural Gas | 2013 | ### 2014 | ### 3 |
| Boiler #7 | 1.0 | 980 scf/hr | Natural Gas | 2013 | ### 2014 | ### 4 |
| Boiler #8 | 1.0 | 980 scf/hr | Natural Gas | 2013 | ### 2014 | ### 5 |
| Boiler #9 | 1.0 | 980 scf/hr | Natural Gas | 2013 | ### 2014 | ### 6 |
| Boiler #10 | 1.34 | 1,314 scf/hr | Natural Gas | 2013 | ### 2014 | ### 7 |
| Boiler #11 | 1.18 | 8.4 gal/hr | Distillate Fuel | 2013 | ### 2014 | ### 1 |

Stationary Engines

| ### Equipment | Max. Input Capacity (MMBtu/hr) | Rated Output Capacity (ekW) | Fuel Type | Firing Rate (gal/hr) | Date of Manuf. | ### Date of Install. |
| --- | --- | --- | --- | --- | --- | --- |
| Generator #1* | 4.4 | 400 | Distillate Fuel | 32 | 2006 | -- |
| Generator #2 | 14.4 | 1,500 | Distillate Fuel | 105 | 2012 | 2012 |
| Generator #3 | 14.4 | 1,500 | Distillate Fuel | 105 | 2012 | 2012 |
| Generator #4 | 14.4 | 1,500 | Distillate Fuel | 105 | 2012 | 2012 |
| Generator #5** | 4.4 | 500 | Distillate Fuel | 36.2 | 2024 | 2025 |

* Removed from License

** New to License

### Definitions

Distillate Fuel means the following:

- Fuel oil that complies with the specifications for fuel oil numbers 1 or 2, as defined by the American Society for Testing and Materials (ASTM) in ASTM D396;

- Diesel fuel oil numbers 1 or 2, as defined in ASTM D975;

- Kerosene, as defined in ASTM D3699;

- Biodiesel, as defined in ASTM D6751; or

- Biodiesel blends, as defined in ASTM D7467.

Records or Logs mean either hardcopy or electronic records.

### Application Classification

All rules, regulations, or statutes referenced in this air emission license refer to the amended version in effect as of the date this license was issued.

The application for MaineGeneral includes the licensing of new equipment. Therefore, the license is considered a renewal of currently licensed emission units and an amendment to add new equipment, and it has been processed through Major and Minor Source Air Emission License Regulations, 06-096 Code of Maine Rules (C.M.R.) ch. 115.

This amendment adds new equipment to the license. Therefore, this amendment is determined to be a minor modification and has been processed as such.

### Facility Classification

With the operating hours restriction on the emergency generators, the facility is licensed as follows:

- As a synthetic minor source of air emissions for criteria pollutants, because MaineGeneral is subject to license restrictions that keep facility emissions below major source thresholds for NOx; and

- As an area source of hazardous air pollutants (HAP), because the licensed emissions are below the major source thresholds for HAP.

## BEST PRACTICAL TREATMENT (BPT)

### Introduction

In order to receive a license, the applicant must control emissions from each unit to a level considered by the Department to represent Best Practical Treatment (BPT), as defined in Definitions Regulation, 06-096 C.M.R. ch. 100. Separate control requirement categories exist for new and existing equipment.

BPT for new sources and modifications requires a demonstration that emissions are receiving Best Available Control Technology (BACT), as defined in Definitions Regulation, 06-096 C.M.R. ch. 100. BACT is a top-down approach to selecting air emission controls considering economic, environmental, and energy impacts.

BPT for existing emissions equipment means that method which controls or reduces emissions to the lowest possible level considering:

- the existing state of technology;

- the effectiveness of available alternatives for reducing emissions from the source being considered; and

- the economic feasibility for the type of establishment involved.

### Boilers #3-#11

MaineGeneral operates nine boilers, Boilers #3-#11, for steam and heat. Boilers #3, #4, and #5 have burners rated at 24.5 MMBtu/hr each, and all three can fire either natural gas or propane. Boilers #6, #7, #8, and #9 have burners rated at 1.0 MMBtu/hr each, and all four exclusively fire natural gas. Boilers #10 and #11 have burners rated at 1.34 MMBtu/hr and 1.18 MMBtu/hr, respectively. Boiler #10 fires natural gas, while Boiler #11 fires distillate fuel. Boilers #3-#5 were all installed in 2012 and exhaust through a shared stack, while Boilers #6-#11 were all installed in 2014, and each exhausts through its own stack.

With limited exceptions, no person shall import, distribute, or offer for sale any distillate fuel with a sulfur content greater than 0.0015% by weight (15 ppm) pursuant to 38 M.R.S.  § 603-A(2)(A)(3). Therefore, the distillate fuel purchased or otherwise obtained for use in Boiler #11 shall not exceed 0.0015% by weight (15 ppm).

##### BPT Findings

The BPT emission limits for Boilers #3, #4, and #5 were based on the following:

| PM/PM10/PM2.5 | – | 0.008 lb/MMBtu based on Manufacturer’s emission factor |
| --- | --- | --- |
| SO2 | – | 0.001 lb/MMBtu based on Manufacturer’s emission factor |
| NOx | – | 0.052 lb/MMBtu based on Manufacturer’s emission factor |
| CO | – | 0.037 lb/MMBtu based on Manufacturer’s emission factor |
| VOC | – | 0.004 lb/MMBtu based on Manufacturer’s emission factor |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BPT emission limits for Boilers #6-#10 were based on the following:

| PM/PM10/PM2.5 | – | 0.05 lb/MMBtu based on 06-096 C.M.R. ch. 115, BPT |
| --- | --- | --- |
| SO2 | – | 0.6 lb/MMscf based on AP-42 Table 1.4-2 dated 7/98 |
| NOx | – | 100 lb/MMscf based on AP-42 Table 1.4-1 dated 7/98 |
| CO | – | 84 lb/MMscf based on AP-42 Table 1.4-1 dated 7/98 |
| VOC | – | 5.5 lb/MMscf based on AP-42 Table 1.4-2 dated 7/98 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BPT emission limits for Boiler #11 were based on the following:

| PM/PM10/PM2.5 | – | 0.08 lb/MMBtu based on 06-096 C.M.R. ch. 115, BPT |
| --- | --- | --- |
| SO2 | – | based on firing distillate fuel with a maximum sulfur content of 0.0015% by weight |
| NOx | – | 20 lb/1,000 gal based on AP-42 Table 1.3-1 dated 5/10 |
| CO | – | 5 lb/1,000 gal based on AP-42 Table 1.3-1 dated 5/10 |
| VOC | – | 0.34 lb/1,000 gal based on AP-42 Table 1.3-3 dated 5/10 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BPT emission limits for Boilers #3-#11 are the following:

| Unit | Pollutant | lb/MMBtu |
| --- | --- | --- |
| Boiler #3 | PM | 0.08 |
| Boiler #4 | PM | 0.08 |
| Boiler #5 | PM | 0.08 |

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler #3 | 0.20 | 0.20 | 0.20 | 0.02 | 1.27 | 0.91 | 0.10 |
| Boiler #4 | 0.20 | 0.20 | 0.20 | 0.02 | 1.27 | 0.91 | 0.10 |
| Boiler #5 | 0.20 | 0.20 | 0.20 | 0.02 | 1.27 | 0.91 | 0.10 |
| Boiler #6 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #7 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #8 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #9 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #10 | 0.07 | 0.07 | 0.07 | -- | 0.13 | 0.11 | 0.01 |
| Boiler #11 | 0.09 | 0.09 | 0.09 | -- | 0.17 | 0.04 | -- |

##### Visible Emissions

Visible emissions from Boilers #3-#10 shall not exceed 10% opacity on a six-minute block average basis.

Visible emissions from Boiler #11 shall not exceed 20% opacity on a six-minute block average basis.

##### Periodic Monitoring

Periodic monitoring for Boilers #3-#11 shall include recordkeeping to document fuel use both on a monthly and calendar year total basis. Documentation shall include the type of fuel used and sulfur content of the fuel, if applicable.

##### New Source Performance Standards (NSPS): 40 C.F.R. Part 60, Subpart Dc

Due to their sizes and years of manufacture, the Boilers #3, #4, and #5 are subject to Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units 40 C.F.R. Part 60, Subpart Dc for units greater than 10 MMBtu/hr manufactured after June 9, 1989. Due to the sizes of Boilers #6-#11, the units are not subject to Subpart Dc. [40 C.F.R. § 60.40c]

MaineGeneral shall comply with all requirements of 40 C.F.R. Part 60, Subpart Dc applicable to Boilers #3, #4, and #5 including, but not limited to, the following:

- Notifications

MaineGeneral was required to submit notification to EPA and the Department of the date of construction, anticipated start-up, and actual start-up. This notification included the design heat input capacity of the boiler and the type of fuel to be combusted. [40 C.F.R. § 60.48c(a)]

- Reporting and Recordkeeping

- MaineGeneral shall maintain records of the amounts of each fuel combusted during each calendar month with fuel certifications. [40 C.F.R. § 60.48c(g)]

- MaineGeneral shall maintain records required by Subpart Dc for a period of two years following the date of the record. [40 C.F.R. § 60.48c(i)] Note: Standard Condition (8) of this license requires all records to be retained for six years; therefore, the two-year record retention requirement of Subpart Dc shall be streamlined to the more stringent six-year requirement.

##### National Emission Standards for Hazardous Air Pollutants (NESHAP): 40 C.F.R. Part 63, Subpart JJJJJJ

Boilers #3-#10 are not subject to the National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources, 40 C.F.R. Part 63, Subpart JJJJJJ. Natural gas-fired and propane-fired units are exempt from the requirements of this regulation. [40 C.F.R. §§ 63.11195(e)]

Boiler #11 is considered a hot water heater and therefore is not subject to the National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources, 40 C.F.R. Part 63, Subpart JJJJJJ. Hot water heaters, as defined in this subpart and including hot water boilers (i.e., those not generating steam) combusting gaseous, liquid, or biomass fuel with a heat input capacity of less than 1.6 million Btu per hour, are not subject to the requirements of this subpart. [40 C.F.R. § 63.11195]

### Generators #2, #3, #4, and #5

MaineGeneral operates four emergency generators, Generators #2, #3, #4, and #5. The emergency generators are generator sets each consisting of an engine and an electrical generator. Emergency Generators #2, #3, and #4 have engines rated at 14.4 MMBtu/hr each, while Emergency Generator #5 has an engine rated at 4.4 MMBtu/hr. All four units fire distillate fuel and were manufactured in 2012, 2012, 2012, and 2024, respectively.

##### BACT and BPT Findings

Note: BACT is for Generator #5; BPT is for Generators #2, #3, and #4.

- Particulate matter (PM, PM10, PM2.5)

MaineGeneral fires only low-ash content fuel, distillate fuel, in Generator #5 and optimizes combustion conditions by following maintenance practices recommended by the manufacturer. Additional add-on pollution controls are not economically feasible.

BACT for PM, PM10, and PM2.5 emissions from Generator #5 is the use of distillate fuel and the emission limits listed in the tables below

- Sulfur Dioxide (SO2)

MaineGeneral fires only distillate fuel in Generator #5. The use of this fuel results in minimal emissions of SO2, and additional add-on pollution controls are not economically feasible.

BACT for SO2 emissions from Generator #5 is the use of ultra-low-sulfur distillate fuel and the emission limits listed in the tables below

- Nitrogen Oxides (NOx)

There are several control strategies for the control of NOx from distillate fuel-fired engines including Selective Catalytic Reduction (SCR), Selective Non-Catalytic Reduction (SNCR), and proper operation and maintenance of the engine.

Both SCR and SNCR are technically feasible control technologies for minimizing NOx. Both methods include injection of a NOx reducing agent, typically ammonia or urea, into the boiler combustion gases, where the reagent reacts with NOx to form nitrogen and water. Each technology is effective within a specific temperature range, 500 – 1,200 °F for SCR and 1,400 – 1,600 °F for SNCR. However, both SCR and SNCR have the negative environmental impact of emissions of unreacted ammonia. In addition, due to the initial capital cost and annual operating costs, these systems are typically only considered cost effective for units larger than Generator #5.

BACT for NOx emissions from Generator #5 is proper maintenance and operation of the unit and the emission limits listed in the tables below.

- Carbon Monoxide (CO)

There are several control strategies for the control of CO and VOC including oxidation catalysts, thermal oxidizers, and use of an oxygen trim system. Both oxidation catalysts and thermal oxidizers have high capital, maintenance, and operational costs considering the size of the generators in question. These controls were determined to be economically infeasible.

BACT for CO and VOC emissions from Generator #5 are the emission limits listed in the tables below.

The BPT emission limits for Generators #2, #3, and #4 are based on the following:

| PM/PM10/PM2.5 | – | 0.12 lb/MMBtu from 06-096 C.M.R. ch. 103 |
| --- | --- | --- |
| SO2 | – | Combustion of distillate fuel with a maximum sulfur content not to exceed 15 ppm (0.0015% sulfur by weight) |
| NOx | – | 29.35 lb/hr based on manufacturers’ “not-to-exceed” data |
| CO | – | 3.85 lb/hr based on manufacturers’ “not-to-exceed” data |
| VOC | – | 0.72 lb/hr based on manufacturers’ “not-to-exceed” data |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BACT emission limits for Generator #5 are based on the following:

| PM/PM10/PM2.5 | – | 0.12 lb/MMBtu from 06-096 C.M.R. ch. 103 |
| --- | --- | --- |
| SO2 | – | Combustion of distillate fuel with a maximum sulfur content not to exceed 15 ppm (0.0015% sulfur by weight) |
| NOx | – | 3.2 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 |
| CO | – | 0.85 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 |
| VOC | – | 0.09 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BACT and BPT emission limits for the Generators #2, #3, #4, and #5 are the following:

| Unit | Pollutant | lb/MMBtu |
| --- | --- | --- |
| Generator #2 | PM | 0.12 |
| Generator #3 | PM | 0.12 |
| Generator #4 | PM | 0.12 |
| Generator #5 | PM | 0.12 |

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator #2 | 1.73 | 1.73 | 1.73 | 0.02 | 29.35 | 3.85 | 0.72 |
| Generator #3 | 1.73 | 1.73 | 1.73 | 0.02 | 29.35 | 3.85 | 0.72 |
| Generator #4 | 1.73 | 1.73 | 1.73 | 0.02 | 29.35 | 3.85 | 0.72 |
| Generator #5 | 0.53 | 0.53 | 0.53 | 0.01 | 14.08 | 3.74 | 0.40 |

Visible emissions from each of the emergency generators shall not exceed 20% opacity on a six-minute block average basis.

BPT for the emergency generators includes recordkeeping of all maintenance conducted on each engine.

##### Chapter 169

Generators #2, #3, and #4 were installed prior to the effective date of Stationary Generators, 06-096 C.M.R. ch. 169 (Chapter 169) and are therefore exempt from this rule pursuant to section 1.

Chapter 169 is applicable to Generator #5. It is an emergency generator powered by an engine with a rated output of less than 1,000 brake horsepower (747 kW). Chapter 169 identifies emission standards for generator engines subject to this chapter and stack height requirements for certain generator engines subject to this chapter.

- Chapter 169 Emission Standards Requirements

For Generator #5, MaineGeneral shall comply with the emission standards for emergency generators by complying with the applicable standards contained in 40 C.F.R. Part 60, Subpart IIII. [06-096 C.M.R. ch. 169, § 4(B)(1)]

- Chapter 169 Stack Height Requirements

Chapter 169 identifies stack height requirements for any stack used to exhaust a generator engine or combination of generator engines with a combined rated output equal to or greater than 1,000 brake horsepower (747 kW). Individual generator engines with a maximum power capacity of less than 300 kW are not included in the assessment of the combined generator power capacity exhausted through a common stack. [06-096 C.M.R. ch. 169, § 6]

There are no stack height requirements in Chapter 169 applicable to Generator #5 because it exhausts through its own stack and its rated output is less than 1,000 brake horsepower (747 kilowatts). [06-096 C.M.R. ch. 169, § 6]

##### New Source Performance Standards

Standards of Performance for Stationary Compression Ignition Internal Combustion Engines, 40 C.F.R. Part 60, Subpart IIII is applicable to Emergency Generators #2, #3, #4, and #5 since the units were ordered after July 11, 2005, and manufactured after April 1, 2006. [40 C.F.R. § 60.4200]

A summary of the currently applicable federal 40 C.F.R. Part 60, Subpart IIII requirements is listed below.

- Emergency Engine Designation and Operating Criteria

Under 40 C.F.R. Part 60, Subpart IIII, a stationary reciprocating internal combustion engine (ICE) is considered an emergency stationary ICE (emergency engine) as long as the engine is operated in accordance with the following criteria.  Operation of an engine outside of the criteria specified below may cause the engine to no longer be considered an emergency engine under 40 C.F.R. Part 60, Subpart IIII, resulting in the engine being subject to requirements applicable to non-emergency engines.

- Emergency Situation Operation (On-Site)

There is no operating time limit on the use of an emergency engine to provide electrical power or mechanical work during an emergency situation.  Examples of use of an emergency engine during emergency situations include the following:

- Use of an engine to produce power for critical networks or equipment (including power supplied to portions of a facility) because of failure or interruption of electric power from the local utility (or the normal power source, if the facility runs on its own power production);

- Use of an engine to mitigate an on-site disaster;

- Use of an engine to pump water in the case of fire, flood, natural disaster, or severe weather conditions; and

- Similar instances.

- Non-Emergency Situation Operation

An emergency engine may be operated up to a maximum of 100 hours per calendar year for maintenance checks, readiness testing, and other non-emergency situations as described below.

- An emergency engine may be operated for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government; the manufacturer; the vendor; the regional transmission organization or equivalent balancing authority and transmission operator; or the insurance company associated with the engine.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency ICE more than 100 hours per calendar year.

- An emergency engine may be operated for up to 50 hours per calendar year for other non-emergency situations.  However, these operating hours are counted as part of the 100 hours per calendar year operating limit described in paragraph (2) and (2) (i) above.

The 50 hours per calendar year operating limit for other non-emergency situations cannot be used for peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 C.F.R. §§ 60.4211(f) and 60.4219]

    - 40 C.F.R. Part 60, Subpart IIII Requirements

- Manufacturer Certification Requirement

The engines shall be certified by the manufacturer as meeting the emission standards for new non-road compression ignition engines found in 40 C.F.R. § 60.4202. [40 C.F.R. § 60.4205(b)]

- Ultra-Low Sulfur Fuel Requirement

The fuel fired in the engines shall not exceed 15 ppm sulfur (0.0015% sulfur).

[40 C.F.R. § 60.4207(b)]

- Non-Resettable Hour Meter Requirement

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4209(a)]

- Operation and Maintenance Requirements

The engines shall be operated and maintained according to the manufacturer’s emission-related written instructions. MaineGeneral may only change those emission-related settings that are permitted by the manufacturer. [40 C.F.R. § 60.4211(a)]

MaineGeneral shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

- Annual Time Limit for Maintenance and Testing

As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). [40 C.F.R. § 60.4211(f)]

- Initial Notification Requirement

No initial notification is required under 40 C.F.R. Part 60, Subpart IIII for emergency engines. [40 C.F.R. § 60.4214(b)]

- Recordkeeping

MaineGeneral shall keep records that include the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time. [40 C.F.R. § 60.4214(b)]

##### National Emissions Standards for hazardous Air Pollutants (NESHAP): 40 C.F.R. Part 63, Subpart ZZZZ

Pursuant to 40 C.F.R. § 60.6590(c), stationary compression ignition engined subject to regulations under 40 C.F.R. Subpart IIII must meet the requirements of Subpart ZZZZ by meeting the requirements of 40 C.F.R. Part 60, Subpart IIII. No further requirements apply for such engines under Subpart ZZZZ. [40 C.F.R. § 63.6590(c)]

### General Process Emissions

Visible emissions from any general process source shall not exceed 20% opacity on a six-minute block average basis.

### Fugitive Emissions

MaineGeneral shall not cause emissions of any fugitive dust during any period of construction, reconstruction, or operation without taking reasonable precautions. Such reasonable precautions shall be included in the facility’s continuing program of best management practices for suppression of fugitive particulate matter. See 06-096 C.M.R. ch. 101, § 4(C) for a list of potential reasonable precautions.

MaineGeneral shall not cause or allow visible emissions within 20 feet of ground level, measured as any level of opacity and not including water vapor, beyond the legal boundary of the property on which such emissions occur. Compliance with this standard shall be determined pursuant to 40 C.F.R. Part 60, Appendix A, Method 22.

### Annual Emissions

The table below provides an estimate of facility-wide annual emissions for the purposes of calculating the facility’s annual air license fee and establishing the facility’s potential to emit (PTE). Only licensed equipment is included, i.e., emissions from insignificant activities are excluded. Similarly, unquantifiable fugitive particulate matter emissions are not included except when required by state or federal regulations. Maximum potential emissions were calculated based on the following assumptions:

- Operating Boilers #3-#11 for 8,760 hrs/yr each; and

- Operating Generators #2-#5 for 100 hrs/yr each of non-emergency operation.

This information does not represent a comprehensive list of license restrictions or permissions. That information is provided in the Order section of this license.

Total Licensed Annual Emissions for the Facility

Tons/year

(used to calculate the annual license fee)

|  | PM | PM10 | PM2.5 | SO2 | NOx | CO | VOC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boilers #3 - #5 | 2.6 | 2.6 | 2.6 | 0.3 | 16.7 | 11.9 | 1.3 |
| Boilers #6 - #9 | 0.9 | 0.9 | 0.9 | 0.1 | 1.7 | 1.4 | 0.1 |
| Boiler #10 | 0.3 | 0.3 | 0.3 | -- | 0.6 | 0.5 | 0.1 |
| Boiler #11 | 0.4 | 0.4 | 0.4 | -- | 0.7 | 0.2 | 0.1 |
| Generators #2 - #4 | 0.3 | 0.3 | 0.3 | -- | 4.4 | 0.6 | 0.1 |
| Generator #5 | 0.1 | 0.1 | 0.1 | -- | 0.8 | 0.2 | 0.1 |
| Total TPY | 4.6 | 4.6 | 4.6 | 0.4 | 24.9 | 14.8 | 1.8 |

| Pollutant | Tons/year |
| --- | --- |
| Single HAP | 7.9 |
| Total HAP | 19.9 |

## AMBIENT AIR QUALITY ANALYSIS

The level of ambient air quality impact modeling required for a minor source is determined by the Department on a case-by-case basis. In accordance with 06-096 C.M.R. ch. 115, an ambient air quality impact analysis is not required for a minor source if the total licensed annual emissions of any pollutant released do not exceed the following levels and there are no extenuating circumstances:

| Pollutant | Tons/Year |
| --- | --- |
| PM10 | 25 |
| PM2.5 | 15 |
| SO2 | 50 |
| NOx | 50 |
| CO | 250 |

The total licensed annual emissions for the facility are below the emission levels contained in the table above and there are no extenuating circumstances; therefore, an ambient air quality impact analysis is not required as part of this license amendment.

This determination is based on information provided by the applicant regarding the expected operation of the proposed Generator #5, and all other licensed emission units. If the Department determines that any parameter (e.g., stack size, configuration, flow rate, emission rates, nearby structures, etc.) deviates from what was included in the application, the Department may require MaineGeneral to submit additional information and may require an ambient air quality impact analysis at that time.

# ORDER

Based on the above Findings and subject to conditions listed below, the Department concludes that the emissions from this source:

- will receive Best Practical Treatment,

- will not violate applicable emission standards, and

- will not violate applicable ambient air quality standards in conjunction with emissions from other sources.

The Department hereby grants Air Emission License Renewal and Amendment A-935-71-G-R/A subject to the following conditions.

Severability. The invalidity or unenforceability of any provision of this License or part thereof shall not affect the remainder of the provision or any other provisions. This License shall be construed and enforced in all respects as if such invalid or unenforceable provision or part thereof had been omitted.

## STANDARD CONDITIONS

- Employees and authorized representatives of the Department shall be allowed access to the licensee’s premises during business hours, or any time during which any emissions units are in operation, and at such other times as the Department deems necessary for the purpose of performing tests, collecting samples, conducting inspections, or examining and copying records relating to emissions (38 M.R.S. § 347-C).

- The licensee shall acquire a new or amended air emission license prior to beginning actual construction of a modification, unless specifically provided for in Chapter 115.

[06-096 C.M.R. ch. 115]

- Approval to construct shall become invalid if the source has not commenced construction within eighteen (18) months after receipt of such approval or if construction is discontinued for a period of eighteen (18) months or more. The Department may extend this time period upon a satisfactory showing that an extension is justified, but may condition such extension upon a review of either the control technology analysis or the ambient air quality standards analysis, or both. [06-096 C.M.R. ch. 115]

- The licensee shall establish and maintain a continuing program of best management practices for suppression of fugitive particulate matter during any period of construction, reconstruction, or operation which may result in fugitive dust, and shall submit a description of the program to the Department upon request. [06-096 C.M.R. ch. 115]

- The licensee shall pay the annual air emission license fee to the Department, calculated pursuant to Title 38 M.R.S. § 353-A. [06-096 C.M.R. ch. 115] Payment of the annual air emission license fee for MaineGeneral is due by the end of February of each year. [38 M.R.S. § 353-A(3)]

- The license does not convey any property rights of any sort, or any exclusive privilege. [06-096 C.M.R. ch. 115]

- The licensee shall maintain and operate all emission units and air pollution systems required by the air emission license in a manner consistent with good air pollution control practice for minimizing emissions. [06-096 C.M.R. ch. 115]

- The licensee shall maintain sufficient records to accurately document compliance with emission standards and license conditions and shall maintain such records for a minimum of six (6) years. The records shall be submitted to the Department upon written request. [06-096 C.M.R. ch. 115]

- The licensee shall comply with all terms and conditions of the air emission license. The filing of an appeal by the licensee, the notification of planned changes or anticipated noncompliance by the licensee, or the filing of an application by the licensee for a renewal of a license or amendment shall not stay any condition of the license.

[06-096 C.M.R. ch. 115]

- The licensee may not use as a defense in an enforcement action that the disruption, cessation, or reduction of licensed operations would have been necessary in order to maintain compliance with the conditions of the air emission license.

[06-096 C.M.R. ch. 115]

- In accordance with the Department’s air emission compliance test protocol and 40 C.F.R. Part 60 or other method approved or required by the Department, the licensee shall:

- Perform stack testing to demonstrate compliance with the applicable emission standards under circumstances representative of the facility’s normal process and operating conditions:

- Within sixty (60) calendar days of receipt of a notification to test from the Department or EPA, if visible emissions, equipment operating parameters, staff inspection, air monitoring or other cause indicate to the Department that equipment may be operating out of compliance with emission standards or license conditions; or

- Pursuant to any other requirement of this license to perform stack testing.

- Install or make provisions to install test ports that meet the criteria of 40 C.F.R. Part 60, Appendix A, and test platforms, if necessary, and other accommodations necessary to allow emission testing; and

- Submit a written report to the Department within thirty (30) days from date of test completion.

[06-096 C.M.R. ch. 115]

- If the results of a stack test performed under circumstances representative of the facility’s normal process and operating conditions indicate emissions in excess of the applicable standards, then:

- Within thirty (30) days following receipt of the written test report by the Department, or another alternative timeframe approved by the Department, the licensee shall re-test the non-complying emission source under circumstances representative of the facility’s normal process and operating conditions and in accordance with the Department’s air emission compliance test protocol and 40 C.F.R. Part 60 or other method approved or required by the Department; and

- The days of violation shall be presumed to include the date of stack test and each and every day of operation thereafter until compliance is demonstrated under normal and representative process and operating conditions, except to the extent that the facility can prove to the satisfaction of the Department that there were intervening days during which no violation occurred or that the violation was not continuing in nature; and

- The licensee may, upon the approval of the Department following the successful demonstration of compliance at alternative load conditions, operate under such alternative load conditions on an interim basis prior to a demonstration of compliance under normal and representative process and operating conditions.

[06-096 C.M.R. ch. 115]

- Notwithstanding any other provisions in the State Implementation Plan approved by the EPA or Section 114(a) of the CAA, any credible evidence may be used for the purpose of establishing whether a person has violated or is in violation of any statute, regulation, or license requirement. [06-096 C.M.R. ch. 115]

- The licensee shall maintain records of malfunctions, failures, downtime, and any other similar change in operation of air pollution control systems or the emissions unit itself that would affect emissions and that is not consistent with the terms and conditions of the air emission license. The licensee shall notify the Department within two (2) days or the next state working day, whichever is later, of such occasions where such changes result in an increase of emissions. The licensee shall report all excess emissions in the units of the applicable emission limitation. [06-096 C.M.R. ch. 115]

- Upon written request from the Department, the licensee shall establish and maintain such records, make such reports, install, use and maintain such monitoring equipment, sample such emissions (in accordance with such methods, at such locations, at such intervals, and in such a manner as the Department shall prescribe), and provide other information as the Department may reasonably require to determine the licensee’s compliance status.

[06-096 C.M.R. ch. 115]

- The licensee shall notify the Department within 48 hours and submit a report to the Department on a quarterly basis if a malfunction or breakdown in any component causes a violation of any emission standard (38 M.R.S. § 605). [06-096 C.M.R. ch. 115]

## SPECIFIC CONDITIONS

#### Boilers #3-#11

- Fuel

- Boilers #3, #4, and #5 are licensed to fire natural gas and propane. Boilers #6, #7, #8, #9, and #10 are all licensed to fire only natural gas. Boiler #11 is licensed to fire distillate fuel. [06-096 C.M.R. ch. 115, BPT]

- The facility shall not purchase or otherwise obtain distillate fuel with a maximum sulfur content that exceeds 0.0015% by weight (15 ppm). [06-096 C.M.R. ch. 115, BPT]

- Compliance shall be demonstrated by fuel records showing the quantity, type, and the percent sulfur of the fuel used (if applicable). Records of annual fuel use shall be kept on a monthly and calendar year basis. Fuel sulfur content compliance shall be demonstrated by fuel delivery receipts from the supplier, a statement from the supplier that the fuel delivered meets Maine’s fuel sulfur content standards, fuel supplier certification, certificate of analysis, or testing of fuel in the tank on-site. [06-096 C.M.R. ch. 115, BPT]

- Emissions shall not exceed the following:

| Emission Unit | Pollutant | lb/MMBtu | Origin and Authority |
| --- | --- | --- | --- |
| Boiler #3 | PM | 0.08 | 06-096 C.M.R. ch. 115, BPT |
| Boiler #4 | PM | 0.08 | 06-096 C.M.R. ch. 115, BPT |
| Boiler #5 | PM | 0.08 | 06-096 C.M.R. ch. 115, BPT |

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT]:

| Emission Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler #3 | 0.20 | 0.20 | 0.20 | 0.02 | 1.27 | 0.91 | 0.10 |
| Boiler #4 | 0.20 | 0.20 | 0.20 | 0.02 | 1.27 | 0.91 | 0.10 |
| Boiler #5 | 0.20 | 0.20 | 0.20 | 0.02 | 1.27 | 0.91 | 0.10 |
| Boiler #6 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #7 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #8 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #9 | 0.05 | 0.05 | 0.05 | -- | 0.10 | 0.08 | 0.01 |
| Boiler #10 | 0.07 | 0.07 | 0.07 | -- | 0.13 | 0.11 | 0.01 |
| Boiler #11 | 0.09 | 0.09 | 0.09 | -- | 0.17 | 0.04 | -- |

- Visible emissions from Boiler #11 shall not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(2)]

- Visible emissions from Boilers #3-#10 shall not exceed 10% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(3)]

- MaineGeneral shall comply with all requirements of 40 C.F.R. Part 60, Subpart Dc applicable to Boilers #3, #4, and #5 including, but not limited to, the following:

Reporting and Recordkeeping

MaineGeneral shall maintain records for Boilers #3, #4, and #5 of the amounts of each fuel combusted during each day or, if applicable, monthly records with fuel certifications. [40 C.F.R. § 60.48c(g)]

#### Generators #2, #3, #4, and #5

- Emergency Generators #2, #3, #4, and #5 are all licensed to fire distillate fuel exclusively. [06-096 C.M.R. ch115, BPT]

- Each of the emergency generator shall be limited to 100 hours of operation per calendar year, excluding operating hours during emergency situations. [06-096 C.M.R. ch. 115, BPT]

- MaineGeneral shall keep records of all maintenance conducted on the engines associated with Generators #2, #3, #4, and #5. [06-096 C.M.R. ch. 115, BPT]

- Emissions shall not exceed the following:

| Unit | Pollutant | lb/MMBtu | Origin and Authority |
| --- | --- | --- | --- |
| Generator #2 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |
| Generator #3 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |
| Generator #4 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT]:

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator #2 | 1.73 | 1.73 | 1.73 | 0.02 | 29.35 | 3.85 | 0.72 |
| Generator #3 | 1.73 | 1.73 | 1.73 | 0.02 | 29.35 | 3.85 | 0.72 |
| Generator #4 | 1.73 | 1.73 | 1.73 | 0.02 | 29.35 | 3.85 | 0.72 |
| Generator #5 | 0.53 | 0.53 | 0.53 | 0.01 | 14.08 | 3.74 | 0.40 |

- Visible Emissions

Visible emissions from each of the emergency generators shall not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(4)]

- The Generators shall meet the applicable requirements of 40 C.F.R. Part 60, Subpart IIII, including the following: [incorporated under 06-096 C.M.R. ch. 115, BPT]

- Manufacturer Certification

The engines shall be certified by the manufacturer as meeting the emission standards for new nonroad compression ignition engines found in § 60.4202. [40 C.F.R. § 60.4205(b)]

- Ultra-Low Sulfur Fuel

The fuel fired in the engines shall not exceed 15 ppm sulfur (0.0015% sulfur). Compliance with the fuel sulfur content limit shall be demonstrated by fuel delivery receipts from the supplier, fuel supplier certification, certificate of analysis, or testing of the fuel in the tank on-site. [40 C.F.R. § 60.4207(b) and 06-096 C.M.R. ch. 115, BPT]

- Non-Resettable Hour Meter

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4209(a)]

- Annual Time Limit for Maintenance and Testing

- As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). These limits are based on a calendar year. Compliance shall be demonstrated by records (electronic or written log) of all engine operating hours. [40 C.F.R. § 60.4211(f) and 06-096 C.M.R. ch. 115, BPT]

- MaineGeneral shall keep records that include the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time.

- Operation and Maintenance

The engines shall be operated and maintained according to the manufacturer’s emission-related written instructions. MaineGeneral may only change those emission-related settings that are permitted by the manufacturer. [40 C.F.R. § 60.4211(a)]

MaineGeneral shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

#### General Process Sources

Visible emissions from any general process source shall not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(B)(4)]

#### Fugitive Emissions

- MaineGeneral shall not cause emissions of any fugitive dust during any period of construction, reconstruction, or operation without taking reasonable precautions. Such reasonable precautions shall be included in the facility’s continuing program of best management practices for suppression of fugitive particulate matter. See 06-096 C.M.R. ch. 101, § 4(C) for a list of potential reasonable precautions.

- MaineGeneral shall not cause or allow visible emissions within 20 feet of ground level, measured as any level of opacity and not including water vapor, beyond the legal boundary of the property on which such emissions occur. Compliance with this standard shall be determined pursuant to 40 C.F.R. Part 60, Appendix A, Method 22.

[06-096 C.M.R. ch. 101, § 4(C)]

#### If the Department determines that any parameter value pertaining to construction and operation of the emissions units, including but not limited to stack size, configuration, flow rate, emission rates, nearby structures, etc., deviates from what was submitted in the application or ambient air quality impact analysis for this air emission license, MaineGeneral may be required to submit additional information. Upon written request from the Department, MaineGeneral shall provide information necessary to demonstrate AAQS will not be exceeded, potentially including submission of an ambient air quality impact analysis or an application to amend this air emission license to resolve any deficiencies and ensure compliance with AAQS. Submission of this information is due within 60 days of the Department’s written request unless otherwise stated in the Department’s letter.

[06-096 C.M.R. ch. 115, § 2(O)]

DONE AND DATED IN AUGUSTA, MAINE THIS 11th DAY OF MARCH, 2026.

DEPARTMENT OF ENVIRONMENTAL PROTECTION

BY:							for

MELANIE LOYZIM, COMMISSIONER

The term of this license shall be ten (10) years from the signature date above.

[Note: If a renewal application, determined as complete by the Department, is submitted prior to expiration of this license, then pursuant to Title 5 M.R.S. § 10002, all terms and conditions of the license shall remain in effect until the Department takes final action on the license renewal application.]

PLEASE NOTE ATTACHED SHEET FOR GUIDANCE ON APPEAL PROCEDURES

Date of initial receipt of application:	11/4/2025

Date of application acceptance:	11/6/2025

This Order prepared by Jack Doran, Bureau of Air Quality.